UV Scanner: Flame scanner shall be U.L. recognized. Scanner housing shall be made of rugged anodized aluminum, have two status LEDs, and connect by means of a military-style quick disconnect fitting.
Physical Desciption: Scanner shall be made of high strength anodized aluminum and mount by means of industry standard 1/2” NPTF connection and include: 
· 3/8” Purge connection
· 5 Pin military-style quick disconnect cable fitting
Electrical Characteristics: Scanner shall be powered by 120 VAC or 24 VDC input power. A 120/230 VAC relay contact shall prove flame. In addition, a flame intensity signal shall be provided with the following outputs depending on the model: 
1. 4-20 mA
2. 0 to 10 VDC
3. Frequency Modulation
[bookmark: _GoBack]Manufacturer: Scanner shall be model 5002-01NC manufactured by Preferred Instruments of Danbury, CT.  
