Multiple Burner Flame Input Module: System shall be capable of monitoring up to 16 flame scanner inputs and providing a single output signal to a separate flame safeguard controller. Input module shall accept flame scanner inputs from a variety of manufacturers and interface with varying flame safeguard controllers. Individual flame signal strength shall be indicated, and first-out annunciation shall be provided to determine which flame signal first fell below adjustable threshold levels. 
Operation: System shall accept UV or flame rods signals from all major scanner manufacturers. The number of flame signals connected, and their trip thresholds shall be DIP switch programmable. The control shall interface with a separate 2 x 16 character LCD display, and provide a single "flame proven" signal to a separate flame safeguard controller. Flame proven logic shall be customizable per the application--programmed at the factory. Historical trending of the last 16 alarm conditions shall be provided. 
[bookmark: _GoBack]Manufacturer: Flame input module shall be Preferred Utilties Mfg. Corp. of Danbury, CT, Quanta-Max system model number 5003-01T (UV sensors) or 5003-03T (flame rods). LCD display shall be Preferred Instruments QD485. Flame safeguard controller, if required, shall be 5004-890, 5004-795, or 5004-M series.  
