The actuator shall be totally enclosed, have a six inch stroke and 150 lbs of push or pull thrust. The drive mechanism shall include a permanently lubricated, continuous duty rated, ball bearing type gear motor to drive an Acme threaded lead screw, travelling nut and thrust ram. The actuator shall include isolated auxiliary open and closed end position proving switches, in addition to isolated adjustable start position switches. Linkage shall include an adjustable drive rod and crank arm. The actuator shall be Hays Cleveland, Danbury, CT, Model Series HC-9130.
