[bookmark: _GoBack]Furnish and install where shown on contract drawings a thermally-actuated fusible element safety switch. Install the switch into a 3 ¼" or 4" round junction box and wire into the burner control circuit. In the event ambient temperature rises above 165° F the fusible element melts to open the contact and stop the burner firing. The fusible element safety switch shall be a Preferred Utilities Mfg. Corp., Danbury, CT, Fusomatic Electric Cut-Off Switch.
