[bookmark: _GoBack]Provide and install, in the tank fill pipe, a  Model 71 Overfill Prevention Valve or Model 61F-Stop Overfill Prevention Valve.  The unit shall have a float operated two stage valve system.  The main valve shall shut-off at approximately 95% of the tank capacity leaving a small bypass valve open to permit hose drain down.  At 5" above main valve shut-off, the bypass valve will close completely to shut off all flow.
