Suggested Specifications
[bookmark: _GoBack]Provide and install in the tank fill pipe a Preferred Utilities Mfg. Corp., Danbury, CT, Model 61F-Stop overfill prevention valve system. The unit shall have a float- operated, two stage valve system. The main valve shall shut-off at approximately 95% of the tank capacity, leaving a small bypass valve open to permit the hose to drain. At 5" above main valve shut-off, the bypass valve will close completely to shut off all flow.
