[bookmark: _GoBack]Provide and install at the bottom of the tank suction stub a fully automatic foot valve suited for service in which drip tight shutoff is required. The body shall be constructed of unleaded bronze with a spring loaded poppet assembly. The foot valve shall be complete with an inlet basket style strainer with a minimum open area ratio of 3 to 1 versus the nominal pipe size. The foot valve shall be rated for a minimum of 150 PSI and shall be a Preferred Utilities Mfg. Corp. Danbury, CT Model 60. Model 60 Single Poppet Foot Valves.
