



 
31-35 South St., Danbury, CT 06480
(203) 743-6741
CUSTOMER:

FLOAT LEVEL SWITCH FABRICATION DATA SHEET
SERIAL NUMBER:

JOB: 

ORDER NO.: 
MODEL NUMBER: PLS-1
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Form 344

SDW NO.:	ORDER DATE: 
SCHEDULED SHIP DATE:

STANDARD SPECIFICATIONS
MOUNTING SIZE	.. 1-1/4” NPT
MATERIAL	BRASS

STEM SIZE	1/2” O.D.
MATERIAL	BRASS

FLOAT MATERIAL	BUNA-N
STOPS	BERYLLIUM COPPER
RETAINING RINGS FLUID S.G	0.5 MIN
REED SWITCH RATING	100W RESISTIVE 120VAC
.	8 VA AC RELAY COIL

WARNING: DO NOT POWER TUNGSTEN LIGHT BULBS

SWITCH LEADS	INDEPENDANT
WIRE	#22 AWG.

OPERATING TEMPERATURE AND PRESSURE
FLUID TEMP		..0-180°F TANK PRESSURE	150 PSI MAX.
ELECTRICAL HOUSING	CAST ALUM. EXP. PROOF
MAXIMUM LENGTH	72 IN.


	STANDARD LEVEL COLOR CODE

	L1
	Red

	L2
	Yellow

	L3
	Blue

	L4
	Brown

	L5
	Orange

	L6
	Gray





A=2” MIN., DISTANCE FROM ACTUATION LEVEL TO MOUNT END

A=3” MIN., DISTANCE BETWEEN ACTUATION LEVELS
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