31-35 South St., Danbury, CT 06480

(203) 743-6741

CUSTOMER:

# FLOAT LEVEL SWITCH FABRICATION DATA SHEET

SERIAL NUMBER:

JOB:

ORDER NO.:

MODEL NUMBER: PLS-1

PREFERRED

UTILITIES MFG CORPORATION

14 NPT

1”

L6

A

L5

L4

L3

LO=L1+2”

L2

B

L1

2”

| ACTUATION LEVEL (INCHES) | Circuit In Tank Empty Condition |  |
| --- | --- | --- |
|  | Select One For Each Level: |  |
|  | Closed | Open |
| L6= |  |  |
| L5= |  |  |
| L4= |  |  |
| L3= |  |  |
| L2= |  |  |
| L1= |  |  |
| Furnish Dimensional Data and Switch Logic in Ascending Level Order |  |  |

FLUID: Diesel

Form 344

SDW NO.:	ORDER DATE:

SCHEDULED SHIP DATE:

STANDARD SPECIFICATIONS

MOUNTING SIZE	.. 1-1/4” NPT

MATERIAL	BRASS

STEM SIZE	1/2” O.D.

MATERIAL	BRASS

FLOAT MATERIAL	BUNA-N

STOPS	BERYLLIUM COPPER

RETAINING RINGS FLUID S.G	0.5 MIN

REED SWITCH RATING	100W RESISTIVE 120VAC

.	8 VA AC RELAY COIL

WARNING: DO NOT POWER TUNGSTEN LIGHT BULBS

SWITCH LEADS	INDEPENDANT

WIRE	#22 AWG.

OPERATING TEMPERATURE AND PRESSURE

FLUID TEMP		..0-180°F TANK PRESSURE	150 PSI MAX.

ELECTRICAL HOUSING	CAST ALUM. EXP. PROOF

MAXIMUM LENGTH	72 IN.

| STANDARD LEVEL COLOR CODE |  |
| --- | --- |
| L1 | Red |
| L2 | Yellow |
| L3 | Blue |
| L4 | Brown |
| L5 | Orange |
| L6 | Gray |

A=2” MIN., DISTANCE FROM ACTUATION LEVEL TO MOUNT END

A=3” MIN., DISTANCE BETWEEN ACTUATION LEVELS

DOC:13-01-03-1001-9